Date:		January 17, 2002

To:		Marketing Letter Distribution List

From:		Worldwide Temperature Marketing

Subject: 	Compatibility matrix -- Model 3144, 3244MV, and 3144P HART Temperature Transmitters

Based on customer and Sales Force feedback, we have combined our Top Tier Temperature Transmitters into one model number.  The Model 3144P comes standard with all the current features of the Model 3144 as well as the advanced diagnostics and functionality of the Model 3244MV HART products.  All these options are field configurable with an updated 275 HART Communicator.  Along with all the standard features of the Model 3144 and 3244MV, the Model 3144P was designed with enhanced EMI rejection and user defined custom alarm level capabilities.  Third party validated metrics are available for Safety Instrumented Systems (SIS).   With the addition of the Model 3144P, the Model 3144 and 3244MV will be phased out.  In order to clarify what each temperature transmitter model entails, we have put together a compatibility matrix.

Compatibility Matrix Overview – This matrix contains a brief description and pictures of the major components to show the differences between them.

Compatibility Matrix of Rosemount Temperature Parts – The three matrices are broken down by model -Model 3144, - Model 3244MV and - Model 3144P.  It lists out all the spare part numbers and which new spare part to order if an older model spare part is requested.

Please note these changes only apply to the Model 3244MV HART.  The Model 3244MVF (Fieldbus) and Model 3244MVW (Profibus PA) are not affected at this time.

If you have any questions regarding this document or the Model 3144P, please contact your Rosemount representative, or in the U.S., call Rosemount Customer Central at 
1-800-999-9307.

_______________________________________________________________

Rosemount Inc.
8200 Market Blvd.
Chanhassen, MN USA 55317
1-800-999-9307 (North America)
952-906-8888 (International)

| Compatibility Matrix Overview – Temperature Transmitters |
| --- |
| Description of Part | Model 3144 | Model 3244MV | Model 3144P |
| Electronics Board |  |  |  |
|  | Alarm and Security jumpers. Meter connection is a 6-pin vertical connection | Alarm and Security jumpers. Meter connection is a 6-pin vertical connection | Alarm and Security switches. 10-pin horizontal meter connection in upper right corner |
| Electronics Housing (No physical housing changes, only tag marking change) |  |  |  |
|  | Permanent Metal Label is marked with 3144 | Permanent Metal Label is marked with 3244MV | Permanent Metal Label is marked with 3144P |
| Terminal Block (No Changes) |  |  |  |
| LCD Indicator |  |  |  |
|  | 6-Pin Connection (on back) - Fail Mode jumper on front of meter | 6-Pin Connection (on back) - Fail Mode jumper on front of meter | 10-Pin Connection (on back) -No jumper on front of meter |

Compatibility Matrix for Rosemount Temperature Spare Parts

| Model 3144 / 3244MV / 3144P Matrix |
| --- |
| Description of Part | Part Number(s) | Compatibility | Issues / Actions New Parts to Order |
| Electronics Modules- Plastic shroud, alarm and security jumpers on electronics. | 03144-3011-0007 | Single sensor input 3144 only No longer available | Order entire electronics module 03144-3111-0001 Existing meter not compatible with new electronics |
| Electronics Modules- Plastic shroud, alarm and security jumpers on electronics. | 03144-3012-1007 | Dual sensor 3244MV Hart only No longer available | Order entire electronics module 03144-3111-0002 Existing meter not compatible with new electronics |
| Electronics Modules- Plastic shroud, alarm and security switches on electronics. | 03144-3111-0001 03144-3111-0002 | Single Sensor configuration for 3144P Dual Sensor configuration for 3144P | 3144P Factory configured Electronics module. Each can be reconfigured in the field with HART communicator |
| Meter Kit (display, mounting hardware, 6-pin connection, cover)- M5 Option | 03144-3020-0001 Aluminum 03144-3020-0011 Stainless steel | Meter Kit for 3144 and 3244MV only | Kit will no longer be available |
| LCD Meter (display, mounting hardware, 6-pin connection)- | 03144-3020-0002 | Meter for 3144 and 3244MV only | Replacement meter will be available for 2 years |
| Meter Kit (display, mounting hardware, 10-pin connection, cover)- M5 Option | 03144-3120-0001 Aluminum 03144-3120-0011 Stainless Steel | Meter Kit for 3144P | Meter Kit for new 3144P, not compatible with current 3144/3244MV electronics |
| LCD Meter (display, mounting hardware, 10-pin connection) | 03144-3120-0002 | Meter for 3144P | Meter for new 3144P, not compatible with current 3144/3244MV electronics |
| Meter Cover Kit (includes cover and o-ring only) | 03144-1043-0001 Aluminum 03144-1043-0011 Stainless Steel | 3144, 3244MV and 3144P | Same for all transmitters – continues to be available |
| B4- Mounting Bracket Kit | 03044-2131-0001 | 3144, 3244MV and 3144P | Same for all transmitters – continues to be available |
| B5- Mounting Bracket Kit | 03144-1081-0001 | 3144, 3244MV and 3144P | Same for all transmitters – continues to be available |
| Screw/ Washer Combination for Sensor/ Power (12 pkg) | 03144-1044-0001 | 3144, 3244MV and 3144P | Same for all transmitters – continues to be available |
| External Ground Lug Assembly | 03144-1047-0001 | 3144, 3244MV and 3144P | Continues to be available, now includes the knurled insert. All hardware required for use now included in this model number. |
| Integral Transient Protector Kit (Terminal screws and transient protectors) | 3144-3040-0001 | 3144, 3244MV | Now order part number 03144-3045-0001. Now includes external ground lug with knurled insert. This new model number is compatible with 3144, 3244MV and 31444P |
| 2-pin Security and Alarm jumper (12 pkg) | 03144-1045-0001 | 3144, 3244MV | Continues to be available |
| 6-pin Meter interconnection header (12 pkg) | 03144-1046-0001 | 3144, 3244MV | No longer available |
| 10-pin Meter interconnection header (12 pkg) | 03144-1146-0001 | 3144P | Connectors for new 3144P meter to new electronics |

| Model 3144, 3244MV and 3144P Housing Cover Matrix |
| --- |
| Although the physical housing on all three units are the same, housing cover spare part numbers were changed based on the changes to labels on the inside of the housing covers. |
| Description of Part | Part Number(s) | Compatibility | Issues / Actions New Parts to Order |
| Housing Covers |  |  |  |
| Housing Cover (Includes o-ring and wiring diagram) | 03144-1042-3101 Aluminum 03144-1042-3111 Stainless Steel | 3144 | Cover label is marked as 3144 No longer available |
| Housing cover (Includes o-ring and wiring diagram) | 03144-1042-3201 Aluminum 03144-1042-3211 Stainless Steel | 3244MV | Cover label is marked 3244MV No longer available |
| Housing cover 3144P (Includes o-ring and wiring diagram) | 03144-1142-0001 Aluminum 03144-1142-0002 Stainless Steel | 3144P | New part number for all 3144, 3244MV and 3144P (Note: Wiring diagrams will be correct, but all label covers will be marked 3144P) |
| O-ring for covers (12 pkg) | 01151-0033-0003 | 3144, 3244MV and 3144P | Same for all transmitter – continues to be available |

| Model 3144, 3244MV and 3144P Housing Kit Matrix |
| --- |
| Although the physical housing on all three units are the same, housing spare part numbers changed based on the metal tag on the top of housing. |
| Description of Part | Part Number(s) | Compatibility | Issues / Actions New Parts to Order |
| Housing Kits (Does not include cover) |  |  |  |
| Housing Kit | 03144-1041-3101 Aluminum 03144-1041-3111 Stainless Steel | 3144 | No longer available |
| Housing Kit with External Ground Lug Assembly | 03144-1041-3102 Aluminum 03144-1041-3112 Stainless Steel | 3144 | No longer available |
| Housing Kit | 03144-1041-3201 Aluminum 03144-1041-3211 Stainless Steel | 3244MV | No longer available |
| Housing Kit with External Ground Lug Assembly | 03144-1041-3202 Aluminum 03144-1041-3212 Stainless Steel | 3244MV | No longer available |
| Housing Kit | 03144-1141-0001 Aluminum 03144-1141-0003 Stainless Steel | 3144P, 3144 and 3244MV | New part number for all 3144, 3244MV and 3144P (Note: Metal tag on housing will be incorrect. All label covers will be marked 3144P) |
| Housing Kit with External Ground Lug Assembly | 03144-1141-0002 Aluminum 03144-1141-0004 Stainless Steel | 3144P, 3144 and 3244MV | New part number for all 3144, 3244MV and 3144P (Note: Metal tag on housing will be incorrect. All label covers will be marked 3144P) |